SECTION 22 1123.13

DOMESTIC-WATER PACKAGED BOOSTER PUMPS

PART 1 – GENERAL

## SUMMARY

## This section includes the following types of systems:

### Variable speed booster pump packages.

- REFERENCED STANDARDS

## National Electrical Code Compliance: Components shall comply with NFPA 70, "National Electrical Code."

## UL Compliance:  Package shall be listed and labeled by UL, and comply with UL QCZJ.  "Packaged Pumping Systems."

## UL Compliance:  Controller shall be listed and labeled by UL, and comply with UL 508A, “Industrial Control Panels.”

## NEMA Compliance:  Electric motors and components shall be listed and labeled NEMA.

## ANSI/HI 1.1-1.4, 1.6 – 2000, Nomenclature, Definitions, Applications, Operation and Testing.

## ANSI/HI 9.6.1-1998, NPSH Margin

## ANSI/HI 9.6.3-1997 Operating Region

## ASTM 48, Standard Specification for Gray Iron Castings

- SUBMITTALS

## General:  In addition to procedures specified in Division 1, comply with the following.

## Tag submitted data with the corresponding designation of that item as scheduled in the construction documents. All information submitted shall be individually "tagged" to easily identify it with the corresponding material or equipment.  Failure to comply with this requirement will result in that item or, at the discretion of the Engineer, all items submitted, being rejected without being reviewed.

## Product data:  Furnish catalog information, manufacturers package curve, rated capacities, final impeller dimensions, and accessories provided for the product indicated.

## A general arrangement drawing showing overall dimensions and all piping layouts.

## Complete submittal data for all major equipment (pumps, motors, valves, electrical controls, etc.).

## An electrical schematic, that provides power and control wiring.

## Sequence of operation.

## Indicate operating point of each pump on curves.

## Furnish composite curve for booster package.

## Operation and Maintenance Data:  Provide installation, operation and maintenance (IOM) manuals on all equipment, including assembly drawings as required for a complete explanation and description of all equipment.

## Include installation instructions, maintenance instructions, assembly views, and replacement parts lists.

## QUALITY ASSURANCE

## Single Source Responsibility: Obtain pumps from a single manufacturer.

## Each booster package shall be hydrostatically and flow tested prior to shipment to verify system integrity.

## Pumps shall operate:

## At specified system fluid temperatures without vapor binding and cavitation.

## With variable speed controller to maintain specified discharge pressure and prevent motor overloads.

## The pump NPSH shall conform to the ANSI/HI 9.6.1-1998 standards for Centrifugal and Vertical Pumps for NPSH Margin.

## Pump pressure ratings shall be at least equal to the system’s maximum operating pressure at point where installed, but not less than specified.

## ASME Compliance:  Comply with ASME B31.9 for piping.

## Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

## Provide certified equipment start-up and, when noted, an on site training session. Pump start-up shall be for the purpose of determining pump rotation, lubrication, voltage, and amperage readings. Start-up shall also include verification of proper electrical connections, pump’s balance, and recording of discharge and suction gauge readings. A copy of the start-up report shall be submitted to the Engineer.

## UL Compliance for Packaged Pumping Systems:

## UL 508, "Industrial Control Equipment."

## UL 508A, "Industrial Control Panels."

## UL 778, "Motor-Operated Water Pumps."

## UL 1995, "Heating and Cooling Equipment."

## DELIVERY, STORAGE, AND HANDLING

## Manufacturer’s Shipping Preparation:  Provide flange covers for protection during shipping.

## Store booster in a dry indoor location.

## Retain shipping flange protective covers and protective coatings during storage.

## Protect bearings and couplings against damage from moisture, sand, grit, and other foreign matter.

PART 2 – PRODUCTS

- VARIABLE SPEED BOOSTER PUMPING PACKAGE

## Subject to compliance with requirements below, provide pumps from one of the following manufacturers:

## Basis of design: HYFAB

### Bell & Gossett

### Other pre-approved manufacturer.

## General Description:  Factory-assembled and tested variable speed domestic water pressure booster system with pumps, piping, isolation and check valves, controls, specialties and accessories mounted on a structural steel base. Pump and electrical protection shall be integrated into the pump controller package.  The package shall be arranged in a compact design to allow it to be moved through a standard 36” doorway.

## Pumps:

## Pumps shall be multistage centrifugal pump unit/s, Model e-SV as manufactured by Goulds Pumps or equal. All pump units shall be from one manufacturer and provided complete including electric motor drive.

## Casing Construction: The pump casing shall be of deep drawn, laser welded AISI 304L stainless steel on pump and/or cast iron pedestal (triplex) with discharge up to two inch.  Pump with larger discharge shall be furnished with cast iron pedestals unless specified to have all stainless construction and shall be capable of withstanding maximum working pressures of 360 psi or 580 psi, based on pump staging and flange selection. Piping connections shall be in-line and shall be compatible with ANSI raised face flanges optional NPT.

## Wear Ring: Wear rings shall be provided within each stage. Wear rings must be self centering and easily replaceable.

## Impeller:   Impellers shall be of enclosed design and constructed of AISI 316L stainless steel. Impellers shall provide internal thrust balance in each stage.

## Diffuser Bowl:  Each stage shall have a bowl with attached diffuser and be constructed of AISI 304L stainless steel.

## Seal Housing:  The seal housing shall be of concave design and shall hold the seal faces below the topmost part of the pump casing.

### Mechanical Seal:  Mechanical seals consisting of high temperature carbon rotating ring, stainless steel spring, silicon carbide graphite filled seat, and viton elastomer.

### Shaft Sleeve and Bearing:  The pump shall have shaft sleeves made of Tungsten Carbide and ceramic bearings. Shaft height shall be set with a standard spacer.

## Electric Motor:  The pump drive motor shall be NEMA standard design TC frame suitable for vertical mounting and close coupled to the pump unit. Motors shall be of standard manufacturers catalog design and must not use special bearings as a thrust handling device. The motor rating shall be as specified on the pressure booster schedule and shall have a 1.15 service factor. Motor enclosure and efficiency shall be as specified on the booster pump schedule.

## Testing:  Each pump shall be hydrostatically tested by the manufacturer in accordance with Hydraulic Institute Standards at a minimum of 350 PSI.  Production performance testing shall also be conducted by the manufacturer on each pump unit. Flow and head shall be measured at three operating to verify performance.

## NPSH:  Unit shall be provided with low NPSH option (NPSHR = 3.5 FT or less) for open system applications.

### Check valves:  Angle style, pilot operated check valves shall be installed on the discharge of each pump. The valve shall have a fusion bonded epoxy coated ductile iron body with a bronze disc.  The check valves shall be able to be serviced or rebuilt without removing them from the pressure booster. Direct acting check valves are not acceptable.

## Isolation Valves:  Two-piece, bronze body, full port ball valves shall be provided to isolate each pump and check valve.

### Thermal protection:  Self contained thermal-relief valves factory set to discharge at 125°F shall be mounted on each pump.

### Piping: All piping shall be constructed from Type 304 stainless steel. Suction and Discharge headers shall be designed and constructed for minimal friction loss.

## Pressure gauges:  Pressure gauges shall be adjustable LED displays. Displays shall be supplied for both the suction and discharge headers.

## Package Base:  The pressure booster base shall be designed and fabricated to provide proper structural support for all attached equipment, and provide for anchorage to the structure.  The base shall include a rigid structural member for pump and motor support. Main members shall be constructed from heavy weight A-36 structural steel members with reinforcing channels for larger boosters. Steel base shall be painted with machinery enamel.

## Control Panel:  Manufacturer shall provide a UL-508A listed complete electrical system including main disconnect, variable speed pump controller, pressure transducers, instrumentation and controls to automatically start, stop and modulate pump speed to smoothly, efficiently and reliably provide pump variable flow rates at a constant discharge pressure. The booster package shall include full pump, motor and drive safety features required to protect the equipment and piping system.

## Main Control Panel:  A door-operated non fused main disconnect shall be provided which shall remove power from the entire pressure booster when switched off.  Each Variable Speed Drive (VFD)/Motor shall be protected by a molded case circuit breaker or MSP enclosed in the main control panel.

### Motor Controller:  NEMA ICS 7.1 variable-frequency, variable torque, solid-state pulse-width modulating type.  VFD protective features shall include:

### Ground fault

### Short Circuit

### Motor overload

### Suction and discharge pressure transducers.

### Pressure transducers shall be utilized for providing all pressure signals for the pump control logic.  Pressure switches are not acceptable.

### Pressure transducer shall be a solid-state bonded strain gage type with an accuracy of plus/minus 1 %.  Transducer shall be constructed of non-ferrous metal suitable for used with domestic water.  Pressure transducers constructed of plastic are not acceptable.

### Transducer shall be rated for package discharge and suction pressures as shown on submittal.

### Pressure transducer shall utilize an M12 type connector to prevent moisture intrusion.

### Temperature Sensor

### A NTC thermistor or RTD shall be used for sensing the booster pumps’ discharge temperatures for temperature limit control logic.     Thermostats are not acceptable.

### The temperature sensor shall be of the immersion type and shall be immersed in water from the pumps’ discharge.  It shall be sealed off by a compression type fitting to prevent accidental dislodgement.

### Controller: Touchscreen variable speed pump logic controller in a NEMA 1 enclosure with door operated disconnect to include, power distribution and overload protection for each AFD and the following control features:

### Unit shall utilize user-friendly front panel programming that displays parameters in clear text.

### Display shall show all system variables in plain English.

### Program settings shall be changeable and stored in non-volatile memory. Program settings shall be retained in memory in the event of loss of power to the controller, without the use of a backup battery.

### System operating pressure shall be clearly displayed in PSI or feet of head for ease of use and to provide an operator friendly interface.

### Additional parameters, where applicable, shall be displayed in units consistent with pumping systems.

### The settings and program in whole or part may be locked out with the use of an operator selectable password. Standard system settings shall include at a minimum the following functions:

### Low suction pressure shutdown with auto restart

### High discharge pressure shutdown with lockout

### High discharge temperature shutdown

### Pump failure alarm

### Constant pressure setting with variable flow capability

### Multiple pump operation with alternation

### Pump starting point with allowable, adjustable pressure drop

### Minimum speed

### No flow standby

### Hydro-pneumatic Tank:

### Furnish hydro-pneumatic tank separately for field installation.

### Furnish tank of size pressure rating and construction specified on pressure booster schedule.

### Furnish hydro-pneumatic tank connection on discharge header with union, isolation valve and drain valve on discharge header of packaged pressure booster.

### Sequence of Operation:

### The pump controller shall receive a 4-20mA signal from each pressure transducer.

### The pressure transducer shall monitor system pressure and provide an analog signal to the pump control software, and allow the VFD motor controller to provide a variable Volts/Hz output to the motor.

### Whenever the pressure drops below the set system pressure, the lead pump shall start and run at speed required to maintain system pressure setpoint (as set by the operator.)  If the pressure setpoint cannot be maintained by one pump, the lag pump shall start to provide the extra flow and pressure automatically.

### When demand decreases to a level which can be met by one pump and an adjustable minimum run-timer has elapsed, the lag pump will be stopped.

### The lead pump shall alternate based on elapsed run time.

### When the system experiences low demand the controller shall test for a no flow condition without the use of external switches or controls.  The controller will stop the lead pump after verifying a zero demand condition exists and a minimum run-timer has elapsed. The hydro-pneumatic tank shall supply water to the system until the pressure falls below the restart pressure, at which point the lead pump shall restart

### All program settings shall be based on centrifugal pump language.

### Program settings shall be password protected.  With proper password entry, settings shall be field adjustable to allow changes by the user.

### DemandSet Control (Optional, requires optional flowmeter): To meet ASHRAE 90.1-2010 standard and building code requirement the variable speed pressure booster shall employ logic that recalculates the setpoint based on the actual system friction loss between booster discharge and the remote critical fixture.  The controller will monitor system demand and continuously change the discharge pressure setpoint based on flow.  The controlling set point and flow shall be displayed on the digital screen.

PART 3 – EXECUTION

- EXAMINATION

## Examine areas, equipment foundations, and conditions, for compliance with requirements for installation tolerances and other conditions affecting performance of pumps.

## Examine rough-in for piping systems to verify actual locations of piping connections prior to installation.

## Examine equipment foundations and/or inertia bases for suitable conditions where pumps are to be installed.

## Correct unsatisfactory conditions prior to installation of pumps.

## INSTALLATION

## General:  Comply with the ANSI/HI 1.4-2000 and manufacturer's written installation and alignment instructions.

## Refer to the drawings for details of booster installation.

## Install booster package in specified location.  Provide access for periodic maintenance, including removal of motors, impellers, and accessories.

## Verify proper pump rotation at start-up.

## Perform start-up procedures per manufacturer’s instructions.

## ADJUSTING

## Adjust pressure and temperature setpoints.

## END OF SECTION 22 1123.13